Appendix 1

| Hot work permit checklist for fire precautions. |  |  |  |
| --- | --- | --- | --- |
| Setting up: | Yes | No | N/A |
| - Fire equipment and systems are in service; |  |  |  |
| - Fire extinguishers/blankets are to hand at points of work; |  |  |  |
| - Fire extinguishers are subject to annual maintenance and are full/charged. |  |  |  |
| - Hot work equipment is in good condition; |  |  |  |
| - Gas containers/flammable liquid containers are to be changed/filled in the open air. Use safety dispensers / containers to store and dispense flammable liquids. |  |  |  |
| - Fire alarm zones silenced/smoke detectors covered and appropriate alternative arrangements for activating the fire alarm are in place and relevant staff have been informed. |  |  |  |
| - Escape routes from place of work are clear, i.e. Not obstructed with work materials |  |  |  |
| - Building users/staff working in the vicinity of, in or near the relevant area of the hot work operation made aware/excluded from hot work zone. |  |  |  |
| Within 15 metres of the work: | Yes | No | N/A |
| - Floors swept, clear of combustibles, wetted down, or covered with non-combustible materials where necessary; |  |  |  |
| - Combustible materials, hazardous or flammable liquids have been removed or are protected with non-combustible curtains, sheets or shields; |  |  |  |
| - All wall and floor openings through which sparks can fall have been covered with non-combustible curtains or sheets; and |  |  |  |
| - Non-combustible materials suspended beneath work to collect sparks. |  |  |  |
| Work on walls and ceilings: | Yes | No | N/A |
| - Any combustible material has been protected against sparks or heat; and |  |  |  |
| - Combustibles moved away from the other side of walls and away from metal through which heat can be transferred. |  |  |  |
| Work on enclosed equipment: (tanks, containers, ducts, dust collectors etc.) | Yes | No | N/A |
| - Equipment cleared of all combustibles and dusts; and |  |  |  |
| - Containers purged of all flammable liquids and vapours. |  |  |  |
| - Confined space precautions undertaken in accordance with Confined Spaces Regulations |  |  |  |
| Work on roofs: | Yes | No | N/A |
| - Two Dry Powder Fire extinguishers available at point of work and at boiler |  |  |  |
| - Bitumen boilers at ground level only |  |  |  |
| - Gas cylinders for boilers at least 3 metres from building |  |  |  |

| Fire watch: | Yes | No | N/A |
| --- | --- | --- | --- |
| - Provided during, and then continuously for 60 minutes on completion of work (or after completion of operations). |  |  |  |
| - Supplied with suitable fire extinguishers/blankets and/or hose reel. |  |  |  |
| - Someone is present in the surrounding area that has been trained in basic firefighting and in sounding the alarm. |  |  |  |
| Final check: | Yes | No | N/A |
| - To be made 60 minutes after completion of any operation; and |  |  |  |
| - If contractors have had access to the roof space, check the openings in roof voids are properly closed and locked. |  |  |  |
| Precautions required for work on highways: | Yes | No | N/A |
| - All LPG cylinders are correctly handled, transported and stored at a safe distance from any sources of heat |  |  |  |
| - All equipment to be in good working order, correctly maintained and free from any gas leakage at hoses, joints etc. |  |  |  |
| - An appropriate size of fire extinguisher of the correct type is available and in good working order at the site of the hot working operation |  |  |  |
| - All appropriate personal protective equipment to be available and worn when doing hot work |  |  |  |
| - A fully stocked first aid box to be available and its whereabouts known to all personnel involved |  |  |  |
| - No hot appliances or naked flame to be left unattended at any time unless adequately screened to prevent unauthorised access |  |  |  |
| - Those carrying containers of hot material must be well protected from moving vehicles and contact with members of the public |  |  |  |
| - Where necessary notices warning of hot working to be prominently displayed |  |  |  |
| Comments: |  |  |  |